{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["HVAC Replacement","Tables"],"not_rendered":{"charts":0,"images":3,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"HVAC Replacement","index":0,"n_rows":26,"n_cols":28,"rows_kept":26,"cut":false,"hidden":false,"merged":[[24,3,24,4],[25,5,25,12],[15,14,16,14],[15,15,16,18],[15,19,16,19],[15,20,16,23],[24,5,24,12],[12,3,12,4],[13,3,13,4],[14,3,14,4],[15,3,15,4],[16,3,16,4],[17,3,17,4],[18,3,18,4],[19,3,19,4],[20,3,20,4],[21,3,21,4],[22,3,22,4],[23,3,23,4],[19,5,19,12],[20,5,20,12],[21,5,21,12],[22,5,22,12],[17,15,18,18],[25,1,25,2],[10,5,10,12],[11,5,11,12],[12,5,12,12],[13,5,13,12],[14,5,14,12],[15,5,15,12],[16,5,16,12],[17,5,17,12],[18,5,18,12],[24,1,24,2],[22,1,22,2],[23,1,23,2],[20,1,20,2],[21,1,21,2],[18,1,18,2],[19,1,19,2],[16,1,16,2],[17,1,17,2],[14,1,14,2],[15,1,15,2],[12,1,12,2],[13,1,13,2],[25,3,25,4],[19,14,20,14],[19,15,20,18],[19,19,20,19],[19,24,20,24],[19,25,20,26],[19,27,20,27],[17,14,18,14],[23,5,23,12],[21,27,22,27],[23,14,24,14],[23,15,24,18],[23,19,24,19],[23,20,23,23],[23,24,24,24],[23,25,24,26],[23,27,24,27],[24,20,24,23],[21,14,22,14],[21,15,22,18],[21,19,22,19],[21,20,22,23],[21,24,22,24],[21,25,22,26],[17,19,18,19],[17,24,18,24],[17,25,18,26],[17,20,17,23],[18,20,18,23],[19,20,20,23],[15,24,16,24],[15,25,16,26],[15,27,16,27],[17,27,18,27],[13,14,14,14],[13,15,14,18],[13,19,14,19],[13,24,14,24],[13,25,14,26],[9,27,10,27],[11,14,12,14],[11,15,12,18],[11,19,12,19],[11,20,12,23],[11,24,12,24],[11,25,12,26],[11,27,12,27],[9,14,10,14],[9,15,10,18],[9,19,10,19],[9,20,10,23],[9,24,10,24],[9,25,10,26],[13,27,14,27],[13,20,14,23],[5,27,6,27],[7,14,8,14],[7,15,8,18],[7,19,8,19],[7,24,8,24],[7,25,8,26],[7,27,8,27],[5,14,6,14],[5,15,6,18],[5,19,6,19],[5,20,6,23],[5,24,6,24],[5,25,6,26],[7,20,7,23],[8,20,8,23],[1,27,2,27],[3,14,4,14],[3,15,4,18],[3,19,4,19],[3,20,4,23],[3,24,4,24],[3,25,4,26],[3,27,4,27],[0,14,0,27],[1,14,2,14],[1,15,2,18],[1,19,2,19],[1,20,2,23],[1,24,2,24],[1,25,2,26],[11,1,11,2],[6,0,6,13],[8,0,8,4],[8,5,8,12],[9,1,9,2],[9,3,9,4],[9,5,9,12],[0,0,0,13],[1,0,1,13],[3,0,3,3],[3,4,3,13],[4,0,4,13],[5,0,5,13],[10,3,10,4],[11,3,11,4],[10,1,10,2]]}
["Replacement of Low Efficiency HVAC Units",null,null,null,null,null,null,null,null,null,null,null,null,null,"Calculations"]
["(Converting from Electric Cooling and Heating to Gas Cooling and Heating)",null,null,null,null,null,null,null,null,null,null,null,null,null,"R)","Cooling Electrical Demand",null,null,null,"=","A * G",null,null,null,"=",{"$f":"B10*B16","v":0},null,"kW"]
[]
["Description of UCRM:",null,null,null,"(Data needed:  use of space, age of units)",null,null,null,null,null,null,null,null,null,"S)","Annual Cooling Energy Consumption",null,null,null,"=","R * C",null,null,null,"=",{"$f":"Z2*B12","v":0},null,"kWh/yr"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"T)","Cooling Demand Savings",null,null,null,"=","R * E",null,null,null,"=",{"$f":"Z2*B14","v":0},null,"kW-mo/yr"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"U)","Equivalent Natural Gas Use for Cooling",null,null,null,"=","A * C * 12,000 Btuh/Ton",null,null,null,"=",{"$f":"(B10*B12*12000)/(B17*1030000)","v":{"$error":"#DIV/0!"}},null,"Mcf/yr"]
["Data needed for calculations",null,null,null,null,"Description",null,null,null,null,null,null,null,"Resource",null,null,null,null,null,null,"H * 1,030,000 Btu/Mcf"]
["A)",null,null,"Tons",null,"Cooling Tonnage to be Replaced",null,null,null,null,null,null,null,null,"V)","Annual Cost for Gas Cooling",null,null,null,"=","U * L",null,null,null,"=",{"$f":"Z8*B21","v":{"$error":"#DIV/0!"}},null,"$/yr"]
["B)",null,null,"kW",null,"Resistance Heating to be Replaced"]
["C)",null,null,"hrs/yr",null,"Cooling Equivalent Full Load Operating Hours",null,null,null,null,null,null,null,"Table 15","W)","Annual Cost for Electrical Cooling",null,null,null,"=","S * J + T * M * N",null,null,null,"=",{"$f":"Z4*B19+Z6*B22*B23","v":0},null,"$/yr"]
["D)",null,null,"hrs/yr",null,"Heating Equivalent Full Load Operating Hours",null,null,null,null,null,null,null,"Table 16"]
["E)",null,null,"mo/yr",null,"Number of Cooling Months",null,null,null,null,null,null,null,null,"X)","Original Annual Heating Energy Use",null,null,null,"=","B * D",null,null,null,"=",{"$f":"B11*B13","v":0},null,"kWh/yr"]
["F)",null,null,"mo/yr",null,"Number of Heating Months"]
["G)",null,null,"kW/Ton",null,"Performance of Existing Cooling Unit",null,null,null,null,null,null,null,"Table 1","Y)","Original Annual Heating Energy Cost",null,null,null,"=","X * K + B * F * O * P",null,null,null,"=",{"$f":"Z14*B20+B11*B15*B24*B25","v":0},null,"$/yr"]
["H)",null,null,"COP",null,"Performance of New Cooling Unit"]
["I)",null,null,"%",null,"Efficiency of Proposed Heating Unit",null,null,null,null,null,null,null,null,"Z)","New Annual Heating Energy Use",null,null,null,"=","X * 3,413 Btuh/kW / I",null,null,null,"=",{"$f":"(Z14*3413/(B18/100))/1030000","v":{"$error":"#DIV/0!"}},null,"Mcf/yr"]
["J)",null,null,"$/kWh",null,"Electrical Energy Rate - Summer",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1,030,000 Btu/Mcf"]
["K)",null,null,"$/kWh",null,"Electrical Energy Rate - Winter",null,null,null,null,null,null,null,null,"AA","New Annual Heating Energy Cost",null,null,null,"=","Z * L",null,null,null,"=",{"$f":"Z18*B21","v":{"$error":"#DIV/0!"}},null,"$/yr"]
["L)",null,null,"$/Mcf",null,"Natural Gas Rate"]
["M)",null,null,"$/kW-mo",null,"Electrical Demand Rate - Summer",null,null,null,null,null,null,null,null,"BB)","Annual Energy Savings",null,null,null,"=","W - V + Y - AA",null,null,null,"=",{"$f":"Z12-Z10+Z16-Z20","v":{"$error":"#DIV/0!"}},null,"$/yr"]
["N)",null,null,null,null,"Demand Diversity - Summer Cool (0.0 to 1.0, Default 0.8)"]
["O)",null,null,"$/kW-mo",null,"Electrical Demand Rate - Winter",null,null,null,null,null,null,null,null,"CC)","Simple Payback",null,null,null,"=","Q",null,null,null,"=",{"$f":"B26/Z22","v":{"$error":"#DIV/0!"}},null,"yrs"]
["P)",null,null,null,null,"Enter Diversity of Winter Demand",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BB"]
["Q)",null,null,"$",null,"Cost of Proposed Unit(s)"]

{"sheet":"Tables","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}